Presray Corporation

Critical Containment Products

P.O. Box 200

Wassaic, NY 12592

Phone: (845) 373-9300

Fax: (845) 855 – 8034

www.presray.com

Email: technicalsupport@presray.com

3-Part CSI Specifications

D5B – Sliding Watertight Door With Pneumatic Seals

These specifications are intended to be used as guidelines for architects and engineers as they establish the requirements for a particular project, and may be modified by them as deemed appropriate.

# Part 1 - General

- 1.01	Description

  - Work Included: Provide special doors(s) factory assembled with frame(s) and hardware in accordance with the contract documents.

- 1.02       Standards

  - Comply with the provisions of (as applicable).

1.   AWS Structural Welding Code.

- ASME Structural Welding Code Section IX.

- 1.03       Submittals

  - Manufacturers Data: Submit installation and maintenance instructions for special door(s).

  - Shop Drawings: Submit shop drawings for special door(s) including dimensioned plans and elevations, details of sections, connections and anchorage, and parts list.

  - Certificates (Optional): Submit certification that the door(s) furnished, or a door of similar design, has been satisfactorily tested to verify that it will withstand the design hydrostatic pressure.

- 1.04       Qualifications

  - Experience: The manufacturer of the special door(s) shall present evidence attesting to at least 5 years of successful experience in the design and manufacture of both the door and the door seal of the types specified.

# Part 2 - Products

- 2.01	Door shall be Model D5B as manufactured by Presray Corporation.

- 2.02	Materials

  - Structural Steel Plates and Shapes: ASTM A36 (options available are type 304 stainless steel, type 316 stainless steel, and type 6061 aluminum).

  - Finish: Brush-off blast clean per SSPC-SP7, prime with one coat rust inhibitive, lead free, red primer.

  - Door Seals: Dual Presray type Pneuma-Seal inflatable gaskets (standard material is fabric reinforced high strength synthetic rubber with outstanding aging resistance; consult Presray in cases of unusual environmental conditions).

  - Seal Controls: Control valve, pressure regulator, pressure gages, and mounting panel, for location on both interior and exterior wall to facilitate sealing of the door from either side. Valves shall be designed to ensure that, in the event of inadvertent damage to either seal, the other will remain sealed.

  - Door Hardware: Trolly track mounting brackets, ball bearing hangers and door pulls. Viewing Panel: Presray type (optional). Push button panic dump valve mounted on interior of door panel for quick release of seal pressure (optional).

- 2.03	Design

  - Watertight door(s) shall be designed with a minimum 2:1 factor of safety based on material yield strength, and shall provide an effective seal against the design pressure.

  - Door shall be designed for manual operation from either side (motorized operation optional).

  - Frame shall include suitable provisions for continuous support of all four edges of the door when the door is in the closed position. The frame at the sill shall form a trench to be recessed in the floor; the back wall of the trench shall provide a surface on which to mount the inflatable seal; the front wall shall act as a stop and provide a continuous support for the bottom edge of the door. (Raised threshold in lieu of trench optional). Frame shall include suitable anchors for embedment in concrete (options available include epoxy anchors for mounting in new masonry block walls, gaskets, bolts and inserts for attachment to existing concrete or block, or the frame ready for welding to existing structure).

- 2.04       Fabrication

- A.	Surface contacting the inflatable seals shall be finished to 63 microinch to maximize sealing.

- 2.05       Inspection and Test

  - All welds on steel assemblies that may be potential “leak path” shall be liquid penetrant inspected in accordance with ASME section VIII Div. of Appendix 8.

  - Finished assembly, or assembly similar in design shall be factory leak tested to verify that it will withstand the design hydrostatic pressure (optional).

# Part 3 — Execution

- 3.01	Installation

  - Install special door in accordance with manufacturer’s instructions and approved shop drawings.

# Part 4 — Warranty

- 4.01	1-year limited against defects and workmanship from date of shipment.