- Differential Pressure Transducer by a Setra Systems, Inc. – Model 269:

- The differential pressure transducer must be a single range product with the ability to measure air pressure ranges as low as 0-0.1 inches uni-directional (or 0.05 bi-directional) with a resolution of 0.0001” WC.

- The differential pressure transducer must have the capability to be ordered as either 1%, 0.4% or 0.25% full scale accuracy.  The non-linearity must be calculated using End-Point method.

- The differential pressure sensor must have the ability to send an analog output of 4 to 20 mA (2-wire) to a system controller

- Must be a capacitive based sensor using a stainless steel sensor

- Must be temperature compensated to 0.01% FS thermal error over the temperature range of 20 F to 140F

- Must be reverse wiring protected

- Calibration of the product must be NIST traceable

- Acceptable Manufacturers:

- The Model 269 should be manufactured by Setra Systems, Inc., Boxborough, MA.  Telephone (978) 263-1400 Fax (978) 264-0292 Web Site www.setra.com