- Differential Room Pressure is to be monitored by a Setra Systems, Inc. – SRIM1:

- The SRIM1 room pressure monitor shall be capable of monitoring the differential pressure between two or three individual spaces at all specified locations on the drawings.  Each monitor shall have an internal differential pressure sensor with the ability to send an analog output of 4 to 20 mA, 0 to 5 VDC, or 0 to 10 VDC to a system controller. The device shall have a display resolution of 0.0001” WC.

- Monitors must utilize a direct pressure sensing device for differential pressure measurement; flows through technologies (i.e. hot wire anemometers) are not acceptable.  The monitor will have an internal pressure sensor and must be provided with a NIST traceable calibration certificate for the internal differential pressure transducer

- Each monitor shall be flush mount design and installed in a standard off-the-shelf electrical wall box with no visible external fasteners; visible screw heads are not acceptable.  The Monitor shall be rated for wipe down cleaning procedures.

- Each Monitor shall have a level of password protection.

- Each Monitor shall have the ability to be set in Negative, Positive, or Neutral status enabled through the on screen setup using a membrane key pad.

- Each Monitor shall be able to be calibrated through the menu options with the touch of a button.

- Each unit must be able to snap-on/snap-off from the housing base, to allow for unit removal (calibration, validation, etc) without removal of plumbing or wires.

- Acceptable Manufacturers:

- The room pressure monitors shall be the SRCM as manufactured by Setra Systems, Inc., Boxborough, MA.  Telephone (978) 263-1400 Fax (978) 264-0292 Web Site www.setra.com