- Remote Measurement Display is to be monitored by a Setra Systems, Inc. - SRMD:

- The SRMD remote measurement display shall be capable of displaying 1 or 2 user defined parameters.  Each parameter shall have the ability to  take in a 0 to 5 VDC or 0 to 10 VDC input and have adjustability to calibrate zero and span accordingly

- Each display shall have 1” characters and a 3-1/2 display that can be seen at a distance of 30 feet.  Each display shall be user selectable to have different back light color for ease of identification.

- Each display shall be flush mountable and be rated for wipe down cleaning procedures, with a metallic or white bezel.

- Each display shall mount in a standard 4-11/16” electrical box with no visible external fasteners, units in custom boxes or external fasteners shall not be considered equal.

- Each display shall be capable of being calibrated by the factory with an remotely mounted wall or duct relative humidity and temperature transducer.  The remote wall or duct relative humidity and temperature transducer shall be the SRH product line manufactured by Setra Systems.

- Each Display shall be capable of being powered by either 24 VDC or 24 VAC.

- Acceptable Manufacturers:

- The remote measurement display shall be the SRMD as manufactured by Setra Systems, Inc., Boxborough, MA.  Telephone (978) 263-1400 Fax (978) 264-0292 Web Site www.setra.com