- The Space/Room Pressure Monitor, SRPM shall be a true dead ended low differential pressure sensor and not a flow based sensor.

- Each SRPM shall have a RGB backlight that clearly and visually indicates the status of the room pressure via a green display for normal, yellow for door status warning and red for alarm conditions.

- The unit shall be configurable through a touch screen menu driven display. The pressure display resolution shall be .0001” WC. The pressure display should have an averaging function to produce stable display outputs for “noisy” pressure  environments.

- Each SRPM shall have a time delay feature settable through the Touch Screen interface to prevent false alarms.

- Each SRPM shall have a latch alarm feature so that alarms must be acknowledged and return to normal operating conditions before the alarm can be silenced

- Each SRPM must be zero and span settings performable through a Touch Screen interface.

- Each SRPM shall have local LEDs for visual indication of normal and alarm conditions and local audible alarm, an alarm acknowledge button and a slider bar indication of the actual pressure relative to the alarm setpoints.

- Each SRPM shall have 2 levels of password protection, one for the supervisor to have total control and a lower level password for the operator to change room modes. The room modes shall be positive, negative or neutral.

- Each SRPM shall have an digital input for door status indication and an alarm relay output to signal a BAS system of an alarm condition or drive a remote annunciator.

- Each SRPM shall have 3 possible analog outputs, 4-20 ma, 0-5 VDC and 0-10 VDC.

- Each SRPM shall be CE, RoHS and CSA C22.2 No. 61010-1-04 safety compliant.

- Each SRPM shall have standard accuracy of +/-.5%FS and optional of +/-0.25%FS.

- The SRPM product line shall have an option for BACnet communications MS/TP ASC

- Each SRPM shall be mountable in an off the shelf 2 gang electrical box with a plaster ring.

Manufacturer

1. The Room Pressure Monitoring System shall be the SRPM as manufactured by Setra Systems Inc., Boxboro, Ma. 01431 Tel. 978 263-1400