## Sheet1
Customer: |  |  |  | Result
Site: |  |  |  | Pass/Fail
Project:
PO / Contract No.:
Supplier Ref No.:
Customer Representative:
Installer Representative:
Witness (Optional)
Ref No. | Test / Inspection | Expected / Acceptable Result | Actual Result | Pass/Fail ( P/F ) | Verification
[5 empty] | Installer | Customer | Witness
1 | System Form (SIF, SCF, MMF) completed & available. Attach copy of each to rear of this commisioning document. | SIF for site, SCF for each string, MMF for each Sentinel.
2 | Confirm Sentinel is powered. | Yellow 'Power' LED lit.
3 | Confirm all m-Senzors are powered and communicating. Visual check of m-Senzor LEDs | Green LEDS should be lit and flashing
4 | Start Configuration software & connect to Sentinel via intended long term method. (Note that where this demands connection from off site, the following tests may be completed on site via RS232 connection, but the long term connection method must be confirmed) | Stable communication link. (Note that commissioning of additional communication hardware is outside the scope of this document. Refer to supplier documentation)
5 | Confirm communication settings - System screen/Communication Options tab, disable 'Notify when alarm' and 'Notify at specified time' | Settings correct to suit required comms method
6 | Confirm network communication and reset poll errors - System screen/LAN Statistics tab (For systems with >1 Sentinel) | Poll errors set to zero.Should not occur.
7 | Confirm Sitename - System screen/System tab | Correct site name set. Same as SIF
8 | Confirm date settings - System Screen/System tab | Correct date set
9 | Confirm charger regime setting | Correct type set
10 | All m-Senzors detected & mapped - Monoblock screen/Configuration tab | Total Measurement Modules online = Total mapped MB
Total mapped MBs = SIF and MMF(s)
11 | Compare sample of live displayed MB voltages against actual MB voltage - Monoblock screen/Statistics tab & voltmeter | Displayed voltage to measured voltage difference +/- 0.2%
12 | Compare sample of MB ohmic value (impedance) readings to a suitable handheld meter like a Hioki or Biddle | Displayed ohmic value to measured ohmic value/impedance difference +/- 5%
13 | Confirm MB limits (limits are optional) - Monoblock screen/Limits tab | MB limit values appropriate | Record limits below (note if not enabled)
Voltage Limits
Temperature limits
Impedance limit
14 | Confirm all Strings configured - String screen/Configuration tab | Number of strings configured = SIF
15 | Confirm all String showing valid voltage - String screen/Statistics tab | Correct string voltage
16 | Confirm String limits - String screen/Limits tab | String limit values appropriate | Record limits below (note if not enabled)
Min. String Voltage
Max. String Voltage
Min. String Voltage - Float Mode
Min. Voltage - Idle mode
Max. Voltage variation
Max. Temperature variation (DegC)
Max. Ohmic variation from string median(%)
17 | Confirm current and temperature sensor mappings and readings for each string - String screen/Configuration tab | Current and temperature sensor allocations all valid and match SCF(s)
18 | Confirm String Limits - Current/Temperature screen | String limit values appropriate | Record limits below (note if not enabled)
Discharge Threshold
Charge Limit
Discharge Limit
Float limit
Temperature limit
19 | Confirm String current | Correct string current
20 | Confirm ambient temperature | Correct ambient temperature
21 | Confirm memories properly configured - Memories screen/Configure Memory tab | Memories formatted
22 | Confirm memory sampling rates | Sampling rates set to cover length of rated backup time
23 | Confirm memories cleared of any invalid data | No logged Capacity or Recharge memories
Long Term memories clear
Medium Term memory clear
24 | Alarms configured to suit site communications - Alarms screen | Alarm outputs set
25 | Alarms cleared | No alarms present | Alarms / No alarms
If alarms still present, record below for customer acceptance
| Discharge test (Recommended) Perform a short discharge test to confirm correct operation of system. Note that this may require site approval. Ensure all all above steps are complete prior to discharge. |  | Test / No Test
26 | Confirm discharge triggered correctly | Check state for all discharging strings changes correctly
Check string voltage for all discharging strings drops correctly
Check current for all discharging strings shows correct reading
Check current for all discharging strings shows correct direction
Confirm capacity memory for all discharging strings triggered and logging correctly
27 | Confirm charge triggered correctly | Check current for all charging strings shows correct direction
Confirm recharge memory triggered and logging correctly
Confirm capacity memory stops logging
28 | Confirm all strings in float state or idle for intermittent type chargers | (note the string float state needs to be present for at least 30 seconds before the Monitors string state changes to Float)
29 | Verify Sentinel port 2 communication if fitted and required for installation | Confirm communication.
30 | Check alarms and clear
31 | Confirm configuration saved
32 | Backup configuration file created
33 | Generate Configuration report | PDF configuration report
34 | Close Configuration software, open Link software and connect to site | Stable communication link
35 | Upload Discharge memory(s) from discharge test. Make sure all discharge data has been received by Link before running the Discharge report. | Successful upload
36 | Generate Discharge report. Attach copy to rear of this document.
37 | Initiate permanent communication | Stable comms link