## Revision
Title: | Sentinel Modbus Port 2 Interface
Document Revision: | F
Modbus Register Map Revision: | 2
Hexadecimal representation: | Hexadecimal numbers are receeded by '0x', for example 35 (decimal) = 0x0023
Copyright ã PowerShield Ltd 2006
Note 1) | This document MUST be sanitised before being used to create the customer Port 2 documentation!
a | Save this document as the new version in 'To Be Released' titled '6300-050D Sentinel Modbus Port 2 Interface (customer).xls', and then perform the following…
b | On the 'Input Registers' tab, delete the 'B1001 name' column
c | On the 'Descrete Input Registers' tab, delete both the 'B1001 name' and 'Comments' columns
d | On the 'Holding Registers' tab, delete the 'B1001 name' column
e | Delete these comments and notes, leave the revision information
Revision Control
Version | Description | Author | Date | Released
A | Initial | Charles | 2005-12-02
B | Updated after review | Charles | 2006-03-20
C | Correct a few errors and typos | Charles | 2006-05-10
D | Addition of registers for impedance data | G Moss | 2008-08-18 | 2008-09-29
E | Improved documentation on the function numbers and hexadecimal representation | G Moss | 2009-03-27

## Input Registers
Input Registers, 16-bit, R/O |  |  | Functions: Read = 0x04
Register |  | Length | Description | Units or Valid Values | B1001 name | Implementation Version | Comments
Hexadecimal | Decimal
0x0001 | 1 | 1 | Modbus register map version | 1 = < 5.4.0, 2 = 5.4.0+ | P2_REG_MAP_VER_REG |  | Update this on next release
0x0002 | 2 | 16 | Site name, 32 bytes ASCII |  | P2_SITE_NAME
0x0012 | 18 | 1 | Number of active alarms | 0 to 96 | P2_NUMBER_OF_ALARMS
0x0013 | 19 | 1 | Software version number | Most significant byte=version in BCD, least significant byte=build number, e.g. 3.4.5 = 3405 Hexadecimal | P2_SOFTWARE_VERSION
0x0014 | 20 | 1 | Low 16 bits of current timestamp | Unix style (if this is close to 0xFFFF wait a bit to avoid wrapping) | P2_CURRENT_DATETIMELO | 5.4.17
0x0015 | 21 | 1 | High 16 bits of current timestamp |  | P2_CURRENT_DATETIMEHI | 5.4.17
0x0016 | 22 | 1 | BBus2 flag | 0=voltage only, 1=impedance | P2_ISBBUS2 | 5.4.17
0x0020 | 32 | 1 | String 1 state | These registers contain the following data values: 0 = Not configured 1 = Float Charge 2 = Charging 3 = Discharge 4 = Idle (5.4.0 or later only) | P2_STRING1_STATE
0x002F | 47 | 1 | String 16 state (5.4.0 or later ends here)
0x003F | 63 | 1 | String 32 state (earler than 5.4.0 only) |  | P2_STRING32_STATE
0x0040 | 64 | 1 | String 1 voltage | 40mV units, 0 to 2621.40V | P2_STRING1_VOLTAGE
0x004F | 79 | 1 | String 16 voltage (5.4.0 or later ends here) | 40mV units, 0 to 2621.40V
0x005F | 95 | 1 | String 32 voltage (earler than 5.4.0 only) | 40mV units, 0 to 2621.40V | P2_STRING32_VOLTAGE
0x0060 | 96 | 1 | Monoblock 1 voltage | mV units, 0=module not responding, 1=under range, 65535=over range | P2_MB1_VOLTAGE
0x055F | 1375 | 1 | Monoblock 1280 voltage | mV units, 0=module not responding, 1=under range, 65535=over range | P2_MB1280_VOLTAGE
0x0560 | 1376 | 2 | String 1 current sensor | Amps. IEEE 754 32 bit floating point number, with the most significant 16-bit word in the first register | P2_STRING1_CURRENT
0x057E | 1406 | 2 | String 16 current sensor (5.4.0 or later ends here) | Amps. IEEE 754 32 bit floating point number, with the most significant 16-bit word in the first register
0x059E | 1438 | 2 | String 32 current sensor (earler than 5.4.0 only) | Amps. IEEE 754 32 bit floating point number, with the most significant 16-bit word in the first register | P2_STRING_CURRENT_END
0x05A0 | 1440 | 1 | String 1 temperature sensor | 0.1 °C per count, 65535=not connected or faulty | P2_STRING1_TEMP |  | Note: error codes vary between Bbus types!
0x05AF | 1455 | 1 | String 16 temperature sensor (5.4.0 or later ends here) | 0.1 °C per count, 65535=not connected or faulty
0x05BF | 1471 | 1 | String 32 temperature sensor (earler than 5.4.0 only) | 0.1 °C per count, 65535=not connected or faulty | P2_STRING32_TEMP
0x05C0 | 1472 | 1 | String 1 first monoblock number | 1 to 1280 | P2_STRING1_FIRST_MB
0x05CF | 1487 | 1 | String 16 first monoblock number | 1 to 1280 (5.4.0 or later ends here)
0x05DF | 1503 | 1 | String 32 first monoblock number | 1 to 1280 | P2_STRING32_FIRST_MB
0x05E0 | 1504 | 1 | String 1 last monoblock number | 1 to 1280 | P2_STRING1_LAST_MB
0x05EF | 1519 | 1 | String 16 last monoblock number | 1 to 1280 (5.4.0 or later ends here)
0x05FF | 1535 | 1 | String 32 last monoblock number | 1 to 1280 | P2_STRING32_LAST_MB
Alarm register details
| Register Offset | Length | Description | Units or Valid Values
| 0 | 1 | Time alarm was triggered - Minutes and Seconds | Seconds in Low Byte, Minutes in High Byte
| 1 | 1 | Time alarm was triggered – Hours
| 2 | 1 | Date alarm was triggered - Day and Month | Day-1 (1st=0) in Low Byte, Month-1 (January=0) in High Byte
| 3 | 1 | Date alarm was triggered – Year | Years since 1900
| 4 | 1 | Alarm sub-category and channel number | High Byte contains the Sub-category of the alarm, which is one of the following value: 0) Not Triggered 1) Low Limit Exceeded 2) High Limit Exceeded 3) Low Limit Exceeded in Discharge 4) High Limit, Discharge 5) Low Limit Exceeded in Charge 6) High Limit, Charge
255 – No sub-category is applicable
For an input alarm (Sentinel only) 1 = Open, 2 = Closed.
Low Byte contains the local channel number that triggered the alarm, if applicable. For an input alarm this is the input number from 1 to 4.
| 5 | 1 | Monitor number and string number | High Byte contains the String number that the alarm is associated with (0 if not applicable) Low Byte contains the number of the monitor that triggered the alarm, if applicable (0=Master Battery Monitor).
| 6 | 1 | Monoblock Number that caused alarm (for Monoblock Alarms), or the number of the Monoblock with the minimum voltage for Monoblock Variation Alarm
| 7 | 1 | Monoblock with the maximum voltage for Monoblock Variation Alarm (not used for other alarms)
| 8 | 1 | Minimum Limit that was active when the alarm was triggered
| 9 | 1 | Maximum Limit that was active when the alarm was triggered
| 10 | 1 | Reserved for Future use
| 11 | 1 | Reserved for Future use
P2_ALARM_DETAILS_START
Register |  | Length | Description | Units or Valid Values | ALARM_SYS_B1000_OFFLINE
Hexadecimal | Decimal
0x1000 | 4096 | 12 | Alarm type 0 Monoblock voltage alarm during Charge or Discharge, alarm details | Refer to "Alarm Details" table above for the format of the 12 registers at each address
0x100C | 4108 | 12 | Alarm type 1 Monoblock voltage alarm when on Float, alarm details
0x1018 | 4120 | 12 | Alarm type 2 Temperature alarm, alarm details
0x1024 | 4132 | 12 | Alarm type 3 Current alarm during Charge, alarm details
0x1030 | 4144 | 12 | Alarm type 4 Current alarm during Discharge, alarm details
0x103C | 4156 | 12 | Alarm type 5 Measurement module communications alarm, alarm details
0x1048 | 4168 | 12 | Alarm type 6 Current alarm when on Float, alarm details
0x1054 | 4180 | 12 | Alarm type 7 Not used
0x1060 | 4192 | 12 | Alarm type 8 Slave monitor off-line, alarm details |  | ALARM_SYS_B1000_OFFLINE
0x106C | 4204 | 12 | Alarm type 9 String voltage alarm during Charge or Discharge, alarm details |  | ALARM_SYS_STRING_VOLT_CHG_DIS
0x1078 | 4216 | 12 | Alarm type 10 String voltage alarm when on Float, alarm details |  | ALARM_SYS_STRING_VOLT_FLT
0x1084 | 4228 | 12 | Alarm type 11 String state change to Discharge, alarm details |  | ALARM_SYS_STRING_DISCHARGE
0x1090 | 4240 | 12 | Alarm type 12 Monoblock voltage variation alarm, alarm details |  | ALARM_SYS_MB_VARIATION
0x109C | 4252 | 12 | Alarm type 13 Logging memory invalid (format required), alarm details |  | ALARM_SYS_MEM_INVALID
0x10A8 | 4264 | 12 | Alarm type 14 Logging memory full, alarm details |  | ALARM_SYS_MEM_FULL
0x10B4 | 4276 | 12 | Alarm type 15 Logging memory nearly full, alarm details |  | ALARM_SYS_MEM_FULL_WARNING
0x10C0 | 4288 | 12 | Alarm type 16 Long term logging memory full, alarm details |  | ALARM_SYS_LTERM_MEM_FULL
0x10CC | 4300 | 12 | Alarm type 17 Long term logging memory nearly full, alarm details |  | ALARM_SYS_LTERM_MEM_FULL_WARNING
0x10D8 | 4312 | 12 | Alarm type 18 Mains failure, alarm details |  | ALARM_SYS_MAINS_FAILURE
0x10E4 | 4324 | 12 | Alarm type 19 String state change to Charge, alarm details |  | ALARM_SYS_STRING_CHARGE
0x10F0 | 4336 | 12 | Alarm type 20 String state change to Float, alarm details |  | ALARM_SYS_STRING_FLOAT
0x10FC | 4348 | 12 | Alarm type 21 Automatic battery test failed to start, alarm details |  | ALARM_SYS_BATTEST_NOT_STARTED
0x1108 | 4360 | 12 | Alarm type 22 Automatic battery test overrun, alarm details |  | ALARM_SYS_BATTEST_OVERRUN
0x1114 | 4372 | 12 | Alarm type 23 Alarm notification failure, alarm details |  | ALARM_SYS_NOTIF_FAIL
0x1120 | 4384 | 12 | Alarm type 24 Monoblock Baseline Impedance exceeded, see alarm details |  | ALARM_SYS_MB_BL_IMPEDANCE
0x112C | 4396 | 12 | Alarm type 25 String variance Impedance exceeded, see alarm details |  | ALARM_SYS_STR_VAR_IMPEDANCE
0x1138 | 4408 | 12 | Alarm type 26 Not used |  | ALARM_SYS_MB_AMB_TEMP
0x1144 | 4420 | 12 | Alarm type 27 Monoblock Post temperate |  | ALARM_SYS_MB_POST_TEMP | 5.4.0
0x1150 | 4432 | 12 | Alarm type 28 Monoblock Post temp variation |  | ALARM_SYS_MB_DIFF_TEMP | 5.4.0
0x115C | 4444 | 12 | Alarm type 29 String state change to idle |  | ALARM_SYS_STRING_IDLE | 5.4.0
0x1168 | 4456 | 12 | Alarm type 30 Monoblock Idle voltage low |  | ALARM_SYS_MD_IDLE_VOLT_LOW | 5.4.0
0x1174 | 4468 | 12 | Alarm type 31 Not used
0x1180 | 4480 | 12 | Input 1 (Master Input 1) alarm details
0x118C | 4492 | 12 | Input 2 (Master Input 2) alarm details
0x1198 | 4504 | 12 | Input 3 (Master Input 3) alarm details
0x11A4 | 4516 | 12 | Input 4 (Master Input 4) alarm details
0x11B0 | 4528 | 12 | Input 5 (Slave 1 Input 1) alarm details
0x11BC | 4540 | 12 | Input 6 (Slave 1 Input 2) alarm details
0x11C8 | 4552 | 12 | Input 7 (Slave 1 Input 3) alarm details
0x11D4 | 4564 | 12 | Input 8 (Slave 1 Input 4) alarm details
0x11E0 | 4576 | 12 | Input 9 (Slave 2 Input 1) alarm details
0x11EC | 4588 | 12 | Input 10 (Slave 2 Input 2) alarm details
0x11F8 | 4600 | 12 | Input 11 (Slave 2 Input 3) alarm details
0x1204 | 4612 | 12 | Input 12 (Slave 2 Input 4) alarm details
0x1210 | 4624 | 12 | Input 13 (Slave 3 Input 1) alarm details
0x121C | 4636 | 12 | Input 14 (Slave 3 Input 2) alarm details
0x1228 | 4648 | 12 | Input 15 (Slave 3 Input 3) alarm details
0x1234 | 4660 | 12 | Input 16 (Slave 3 Input 4) alarm details
0x1240 | 4672 | 12 | Input 17 (Slave 4 Input 1) alarm details
0x124C | 4684 | 12 | Input 18 (Slave 4 Input 2) alarm details
0x1258 | 4696 | 12 | Input 19 (Slave 4 Input 3) alarm details
0x1264 | 4708 | 12 | Input 20 (Slave 4 Input 4) alarm details
0x1270 | 4720 | 12 | Input 21 (Slave 5 Input 1) alarm details
0x127C | 4732 | 12 | Input 22 (Slave 5 Input 2) alarm details
0x1288 | 4744 | 12 | Input 23 (Slave 5 Input 3) alarm details
0x1294 | 4756 | 12 | Input 24 (Slave 5 Input 4) alarm details
0x12A0 | 4768 | 12 | Input 25 (Slave 6 Input 1) alarm details
0x12AC | 4780 | 12 | Input 26 (Slave 6 Input 2) alarm details
0x12B8 | 4792 | 12 | Input 27 (Slave 6 Input 3) alarm details
0x12C4 | 4804 | 12 | Input 28 (Slave 6 Input 4) alarm details
0x12D0 | 4816 | 12 | Input 29 (Slave 7 Input 1) alarm details
0x12DC | 4828 | 12 | Input 30 (Slave 7 Input 2) alarm details
0x12E8 | 4840 | 12 | Input 31 (Slave 7 Input 3) alarm details
0x12F4 | 4852 | 12 | Input 32 (Slave 7 Input 4) alarm details
0x1300 | 4864 | 12 | Input 33 (Slave 8 Input 1) alarm details
0x130C | 4876 | 12 | Input 34 (Slave 8 Input 2) alarm details
0x1318 | 4888 | 12 | Input 35 (Slave 8 Input 3) alarm details |  |  | 5.2.12
0x1324 | 4900 | 12 | Input 36 (Slave 8 Input 4) alarm details |  |  | 5.2.12
0x1330 | 4912 | 12 | Input 37 (Slave 9 Input 1) alarm details
0x133C | 4924 | 12 | Input 38 (Slave 9 Input 2) alarm details |  |  | 5.4.0
0x1348 | 4936 | 12 | Input 39 (Slave 9 Input 3) alarm details |  |  | 5.4.0
0x1354 | 4948 | 12 | Input 40 (Slave 9 Input 4) alarm details |  |  | 5.4.0
0x1360 | 4960 | 12 | Input 41 (Slave 10 Input 1) alarm details |  |  | 5.4.0
0x136C | 4972 | 12 | Input 42 (Slave 10 Input 2) alarm details
0x1378 | 4984 | 12 | Input 43 (Slave 10 Input 3) alarm details
0x1384 | 4996 | 12 | Input 44 (Slave 10 Input 4) alarm details
0x1390 | 5008 | 12 | Input 45 (Slave 11 Input 1) alarm details
0x139C | 5020 | 12 | Input 46 (Slave 11 Input 2) alarm details
0x13A8 | 5032 | 12 | Input 47 (Slave 11 Input 3) alarm details
0x13B4 | 5044 | 12 | Input 48 (Slave 11 Input 4) alarm details
0x13C0 | 5056 | 12 | Input 49 (Slave 12 Input 1) alarm details
0x13CC | 5068 | 12 | Input 50 (Slave 12 Input 2) alarm details
0x13D8 | 5080 | 12 | Input 51 (Slave 12 Input 3) alarm details
0x13E4 | 5092 | 12 | Input 52 (Slave 12 Input 4) alarm details
0x13F0 | 5104 | 12 | Input 53 (Slave 13 Input 1) alarm details
0x13FC | 5116 | 12 | Input 54 (Slave 13 Input 2) alarm details
0x1408 | 5128 | 12 | Input 55 (Slave 13 Input 3) alarm details
0x1414 | 5140 | 12 | Input 56 (Slave 13 Input 4) alarm details
0x1420 | 5152 | 12 | Input 57 (Slave 14 Input 1) alarm details
0x142C | 5164 | 12 | Input 58 (Slave 14 Input 2) alarm details
0x1438 | 5176 | 12 | Input 59 (Slave 14 Input 3) alarm details
0x1444 | 5188 | 12 | Input 60 (Slave 14 Input 4) alarm details
0x1450 | 5200 | 12 | Input 61 (Slave 15 Input 1) alarm details
0x145C | 5212 | 12 | Input 62 (Slave 15 Input 2) alarm details
0x1468 | 5224 | 12 | Input 63 (Slave 15 Input 3) alarm details
0x1474 | 5236 | 12 | Input 64 (Slave 15 Input 4) alarm details
0x1480 | 5248
Ohmic Value information
0x2000 | 8192 |  | Monoblock 1 Ohmic value | Value in uOhms, or result error code as detailed: 1) 65535 (0xFFFF) – math overflow 2) 65534 (0xFFFE) – measurement in progress 3) 65533 (0xFFFD) – ADC overrange detected during measurement 4) 65532 (0xFFFC) – calibration factor out of range 5) 65531 (0xFFFB) – no valid result (not measured yet) 6) 65530 (0xFFFA) – ADC overrange detected during gain check (too much ripple) 7) 65529 (0xFFF9) – supply voltage issue 8) 65528 (0xFFF8) – ADC overrange detected during auto calibration 9) 65527 (0xFFF7) – ambient too high 10) 65526 (0xFFF6) – ambient too cold or thermistor fault
0x24FF | 9471 |  | Monoblock 1280 Ohmic value
P2_MB1_IMPEDANCE
P2_MB1280_IMPEDANCE
Post Temp Information
0x2500 | 9472 |  | Monoblock 1 Post temperature
0x29FF | 10751 |  | Monoblock 1280 Post temperature | Value in degrees (signed) or error code: 0xFc17 64535 maths overflow 0xFc16 64534 measurement in progress 0xFc15 64533 result over range 0xFc14 64532 result under range 0xFc13 64531 (B1001) Value not yet read 0xFc12 64530 thermistor low in value or shorted 0xFc11 64529 thermistor high in value or open circuit 0xFc10 64528 channel invalid
P2_MB1_POSTTEMP
P2_MB1280_POSTTEMP
5.2.15
5.4.2

## Discrete Input Registers
Descrete Inputs, 1-bit, R/O |  |  | Functions: Read = 0x02
Register |  | Length | Description | Valid Values | B1001 name | Implementation Version | Comments
Hexadecimal | Decimal
0x0001 | 1 | 1 | Status of alarm type 0 Monoblock voltage alarm during Charge or Discharge | 0=inactive, 1=active
0x0002 | 2 | 1 | Status of alarm type 1 Monoblock voltage alarm when on Float | 0=inactive, 1=active
0x0003 | 3 | 1 | Status of alarm type 2 Temperature alarm | 0=inactive, 1=active
0x0004 | 4 | 1 | Status of alarm type 3 Current alarm during Charge | 0=inactive, 1=active
0x0005 | 5 | 1 | Status of alarm type 4 Current alarm during Discharge | 0=inactive, 1=active
0x0006 | 6 | 1 | Status of alarm type 5 Measurement module communications alarm | 0=inactive, 1=active
0x0007 | 7 | 1 | Status of alarm type 6 Current alarm when on Float | 0=inactive, 1=active
0x0008 | 8 | 1 | Status of alarm type 7 Not used | 0=inactive, 1=active
0x0009 | 9 | 1 | Status of alarm type 8 Slave monitor off-line | 0=inactive, 1=active | ALARM_SYS_B1000_OFFLINE
0x000A | 10 | 1 | Status of alarm type 9 String voltage alarm during Charge or Discharge | 0=inactive, 1=active | ALARM_SYS_STRING_VOLT_CHG_DIS
0x000B | 11 | 1 | Status of alarm type 10 String voltage alarm when on Float | 0=inactive, 1=active | ALARM_SYS_STRING_VOLT_FLT
0x000C | 12 | 1 | Status of alarm type 11 String state change to Discharge | 0=inactive, 1=active | ALARM_SYS_STRING_DISCHARGE
0x000D | 13 | 1 | Status of alarm type 12 Monoblock voltage variation alarm | 0=inactive, 1=active | ALARM_SYS_MB_VARIATION
0x000E | 14 | 1 | Status of alarm type 13 Logging memory invalid (format required) | 0=inactive, 1=active | ALARM_SYS_MEM_INVALID
0x000F | 15 | 1 | Status of alarm type 14 Logging memory full | 0=inactive, 1=active | ALARM_SYS_MEM_FULL
0x0010 | 16 | 1 | Status of alarm type 15 Logging memory nearly full | 0=inactive, 1=active | ALARM_SYS_MEM_FULL_WARNING
0x0011 | 17 | 1 | Status of alarm type 16 Long term logging memory full | 0=inactive, 1=active | ALARM_SYS_LTERM_MEM_FULL |  | THIS ALARM MAPS TO 7 IN LOCAL ALARMS!!!
0x0012 | 18 | 1 | Status of alarm type 17 Long term logging memory nearly full | 0=inactive, 1=active | ALARM_SYS_LTERM_MEM_FULL_WARNING |  | THIS ALARM MAPS TO 8 IN LOCAL ALARMS!!!
0x0013 | 19 | 1 | Status of alarm type 18 Mains failure | 0=inactive, 1=active | ALARM_SYS_MAINS_FAILURE
0x0014 | 20 | 1 | Status of alarm type 19 String state change to Charge | 0=inactive, 1=active | ALARM_SYS_STRING_CHARGE
0x0015 | 21 | 1 | Status of alarm type 20 String state change to Float | 0=inactive, 1=active | ALARM_SYS_STRING_FLOAT
0x0016 | 22 | 1 | Status of alarm type 21 Automatic battery test failed to start | 0=inactive, 1=active | ALARM_SYS_BATTEST_NOT_STARTED
0x0017 | 23 | 1 | Status of alarm type 22 Automatic battery test overrun | 0=inactive, 1=active | ALARM_SYS_BATTEST_OVERRUN
0x0018 | 24 | 1 | Status of alarm type 23 Alarm notification failure | 0=inactive, 1=active | ALARM_SYS_NOTIF_FAIL
0x0019 | 25 | 1 | Status of alarm type 24 Monoblock baseline impedance exceeded | 0=inactive, 1=active | ALARM_SYS_MB_BL_IMPEDANCE | 5.2.15 | THIS ALARM MAPS TO 9 IN LOCAL ALARMS!!!
0x001A | 26 | 1 | Status of alarm type 25 String variance impedance exceeded | 0=inactive, 1=active | ALARM_SYS_STR_VAR_IMPEDANCE | 5.2.15
0x001B | 27 | 1 | Status of alarm type 26 Not used | 0=inactive, 1=active | ALARM_SYS_MB_AMB_TEMP |  | THIS ALARM MAPS TO 10 IN LOCAL ALARMS!!! Monoblock ambient temperature limits exceeded
0x001C | 28 | 1 | Status of alarm type 27 Monoblock Post Temperature | 0=inactive, 1=active | ALARM_SYS_MB_POST_TEMP | 5.4.0 | THIS ALARM MAPS TO 11 IN LOCAL ALARMS!!! Monoblock post temperature limits exceeded
0x001D | 29 | 1 | Status of alarm type 28 Monoblock Post Temp variation | 0=inactive, 1=active | ALARM_SYS_MB_DIFF_TEMP | 5.4.0 | THIS ALARM MAPS TO 12 IN LOCAL ALARMS!!! (Unsure of use)
0x001E | 30 | 1 | Status of alarm type 29 String state change to Idle | 0=inactive, 1=active | ALARM_SYS_STRING_IDLE | 5.4.0
0x001F | 31 | 1 | Status of alarm type 30 Monoblock idle voltage low | 0=inactive, 1=active | ALARM_SYS_MB_IDLE_VOLT_LOW | 5.4.0
0x0020 | 32 | 1 | Status of alarm type 31 Not used | 0=inactive, 1=active
0x0021 | 33 | 1 | Input 1 (Master Input 1) alarm status | 0=inactive, 1=active
0x0022 | 34 | 1 | Input 2 (Master Input 2) alarm status | 0=inactive, 1=active
0x0023 | 35 | 1 | Input 3 (Master Input 3) alarm status | 0=inactive, 1=active
0x0024 | 36 | 1 | Input 4 (Master Input 4) alarm status | 0=inactive, 1=active
0x0025 | 37 | 1 | Input 5 (Slave 1 Input 1) alarm status | 0=inactive, 1=active
0x0026 | 38 | 1 | Input 6 (Slave 1 Input 2) alarm status | 0=inactive, 1=active
0x0027 | 39 | 1 | Input 7 (Slave 1 Input 3) alarm status | 0=inactive, 1=active
0x0028 | 40 | 1 | Input 8 (Slave 1 Input 4) alarm status | 0=inactive, 1=active
0x0029 | 41 | 1 | Input 9 (Slave 2 Input 1) alarm status | 0=inactive, 1=active
0x002A | 42 | 1 | Input 10 (Slave 2 Input 2) alarm status | 0=inactive, 1=active
0x002B | 43 | 1 | Input 11 (Slave 2 Input 3) alarm status | 0=inactive, 1=active
0x002C | 44 | 1 | Input 12 (Slave 2 Input 4) alarm status | 0=inactive, 1=active
0x002D | 45 | 1 | Input 13 (Slave 3 Input 1) alarm status | 0=inactive, 1=active
0x002E | 46 | 1 | Input 14 (Slave 3 Input 2) alarm status | 0=inactive, 1=active
0x002F | 47 | 1 | Input 15 (Slave 3 Input 3) alarm status | 0=inactive, 1=active
0x0030 | 48 | 1 | Input 16 (Slave 3 Input 4) alarm status | 0=inactive, 1=active
0x0031 | 49 | 1 | Input 17 (Slave 4 Input 1) alarm status | 0=inactive, 1=active
0x0032 | 50 | 1 | Input 18 (Slave 4 Input 2) alarm status | 0=inactive, 1=active
0x0033 | 51 | 1 | Input 19 (Slave 4 Input 3) alarm status | 0=inactive, 1=active
0x0034 | 52 | 1 | Input 20 (Slave 4 Input 4) alarm status | 0=inactive, 1=active
0x0035 | 53 | 1 | Input 21 (Slave 5 Input 1) alarm status | 0=inactive, 1=active
0x0036 | 54 | 1 | Input 22 (Slave 5 Input 2) alarm status | 0=inactive, 1=active
0x0037 | 55 | 1 | Input 23 (Slave 5 Input 3) alarm status | 0=inactive, 1=active
0x0038 | 56 | 1 | Input 24 (Slave 5 Input 4) alarm status | 0=inactive, 1=active
0x0039 | 57 | 1 | Input 25 (Slave 6 Input 1) alarm status | 0=inactive, 1=active
0x003A | 58 | 1 | Input 26 (Slave 6 Input 2) alarm status | 0=inactive, 1=active
0x003B | 59 | 1 | Input 27 (Slave 6 Input 3) alarm status | 0=inactive, 1=active
0x003C | 60 | 1 | Input 28 (Slave 6 Input 4) alarm status | 0=inactive, 1=active
0x003D | 61 | 1 | Input 29 (Slave 7 Input 1) alarm status | 0=inactive, 1=active
0x003E | 62 | 1 | Input 30 (Slave 7 Input 2) alarm status | 0=inactive, 1=active
0x003F | 63 | 1 | Input 31 (Slave 7 Input 3) alarm status | 0=inactive, 1=active
0x0040 | 64 | 1 | Input 32 (Slave 7 Input 4) alarm status | 0=inactive, 1=active
0x0041 | 65 | 1 | Input 33 (Slave 8 Input 1) alarm status | 0=inactive, 1=active
0x0042 | 66 | 1 | Input 34 (Slave 8 Input 2) alarm status | 0=inactive, 1=active
0x0043 | 67 | 1 | Input 35 (Slave 8 Input 3) alarm status | 0=inactive, 1=active
0x0044 | 68 | 1 | Input 36 (Slave 8 Input 4) alarm status | 0=inactive, 1=active
0x0045 | 69 | 1 | Input 37 (Slave 9 Input 1) alarm status | 0=inactive, 1=active
0x0046 | 70 | 1 | Input 38 (Slave 9 Input 2) alarm status | 0=inactive, 1=active
0x0047 | 71 | 1 | Input 39 (Slave 9 Input 3) alarm status | 0=inactive, 1=active
0x0048 | 72 | 1 | Input 40 (Slave 9 Input 4) alarm status | 0=inactive, 1=active
0x0049 | 73 | 1 | Input 41 (Slave 10 Input 1) alarm status | 0=inactive, 1=active
0x004A | 74 | 1 | Input 42 (Slave 10 Input 2) alarm status | 0=inactive, 1=active
0x004B | 75 | 1 | Input 43 (Slave 10 Input 3) alarm status | 0=inactive, 1=active
0x004C | 76 | 1 | Input 44 (Slave 10 Input 4) alarm status | 0=inactive, 1=active
0x004D | 77 | 1 | Input 45 (Slave 11 Input 1) alarm status | 0=inactive, 1=active
0x004E | 78 | 1 | Input 46 (Slave 11 Input 2) alarm status | 0=inactive, 1=active
0x004F | 79 | 1 | Input 47 (Slave 11 Input 3) alarm status | 0=inactive, 1=active
0x0050 | 80 | 1 | Input 48 (Slave 11 Input 4) alarm status | 0=inactive, 1=active
0x0051 | 81 | 1 | Input 49 (Slave 12 Input 1) alarm status | 0=inactive, 1=active
0x0052 | 82 | 1 | Input 50 (Slave 12 Input 2) alarm status | 0=inactive, 1=active
0x0053 | 83 | 1 | Input 51 (Slave 12 Input 3) alarm status | 0=inactive, 1=active
0x0054 | 84 | 1 | Input 52 (Slave 12 Input 4) alarm status | 0=inactive, 1=active
0x0055 | 85 | 1 | Input 53 (Slave 13 Input 1) alarm status | 0=inactive, 1=active
0x0056 | 86 | 1 | Input 54 (Slave 13 Input 2) alarm status | 0=inactive, 1=active
0x0057 | 87 | 1 | Input 55 (Slave 13 Input 3) alarm status | 0=inactive, 1=active
0x0058 | 88 | 1 | Input 56 (Slave 13 Input 4) alarm status | 0=inactive, 1=active
0x0059 | 89 | 1 | Input 57 (Slave 14 Input 1) alarm status | 0=inactive, 1=active
0x005A | 90 | 1 | Input 58 (Slave 14 Input 2) alarm status | 0=inactive, 1=active
0x005B | 91 | 1 | Input 59 (Slave 14 Input 3) alarm status | 0=inactive, 1=active
0x005C | 92 | 1 | Input 60 (Slave 14 Input 4) alarm status | 0=inactive, 1=active
0x005D | 93 | 1 | Input 61 (Slave 15 Input 1) alarm status | 0=inactive, 1=active
0x005E | 94 | 1 | Input 62 (Slave 15 Input 2) alarm status | 0=inactive, 1=active
0x005F | 95 | 1 | Input 63 (Slave 15 Input 3) alarm status | 0=inactive, 1=active
0x0060 | 96 | 1 | Input 64 (Slave 15 Input 4) alarm status | 0=inactive, 1=active
0x0061 | 97 | 1 | Input 1 (Master Input 1) contact status | 0=open, 1=closed
0x0062 | 98 | 1 | Input 2 (Master Input 2) contact status | 0=open, 1=closed
0x0063 | 99 | 1 | Input 3 (Master Input 3) contact status | 0=open, 1=closed
0x0064 | 100 | 1 | Input 4 (Master Input 4) contact status | 0=open, 1=closed
0x0065 | 101 | 1 | Input 5 (Slave 1 Input 1) contact status | 0=open, 1=closed
0x0066 | 102 | 1 | Input 6 (Slave 1 Input 2) contact status | 0=open, 1=closed
0x0067 | 103 | 1 | Input 7 (Slave 1 Input 3) contact status | 0=open, 1=closed
0x0068 | 104 | 1 | Input 8 (Slave 1 Input 4) contact status | 0=open, 1=closed
0x0069 | 105 | 1 | Input 9 (Slave 2 Input 1) contact status | 0=open, 1=closed
0x006A | 106 | 1 | Input 10 (Slave 2 Input 2) contact status | 0=open, 1=closed
0x006B | 107 | 1 | Input 11 (Slave 2 Input 3) contact status | 0=open, 1=closed
0x006C | 108 | 1 | Input 12 (Slave 2 Input 4) contact status | 0=open, 1=closed
0x006D | 109 | 1 | Input 13 (Slave 3 Input 1) contact status | 0=open, 1=closed
0x006E | 110 | 1 | Input 14 (Slave 3 Input 2) contact status | 0=open, 1=closed
0x006F | 111 | 1 | Input 15 (Slave 3 Input 3) contact status | 0=open, 1=closed
0x0070 | 112 | 1 | Input 16 (Slave 3 Input 4) contact status | 0=open, 1=closed
0x0071 | 113 | 1 | Input 17 (Slave 4 Input 1) contact status | 0=open, 1=closed
0x0072 | 114 | 1 | Input 18 (Slave 4 Input 2) contact status | 0=open, 1=closed
0x0073 | 115 | 1 | Input 19 (Slave 4 Input 3) contact status | 0=open, 1=closed
0x0074 | 116 | 1 | Input 20 (Slave 4 Input 4) contact status | 0=open, 1=closed
0x0075 | 117 | 1 | Input 21 (Slave 5 Input 1) contact status | 0=open, 1=closed
0x0076 | 118 | 1 | Input 22 (Slave 5 Input 2) contact status | 0=open, 1=closed
0x0077 | 119 | 1 | Input 23 (Slave 5 Input 3) contact status | 0=open, 1=closed
0x0078 | 120 | 1 | Input 24 (Slave 5 Input 4) contact status | 0=open, 1=closed
0x0079 | 121 | 1 | Input 25 (Slave 6 Input 1) contact status | 0=open, 1=closed
0x007A | 122 | 1 | Input 26 (Slave 6 Input 2) contact status | 0=open, 1=closed
0x007B | 123 | 1 | Input 27 (Slave 6 Input 3) contact status | 0=open, 1=closed
0x007C | 124 | 1 | Input 28 (Slave 6 Input 4) contact status | 0=open, 1=closed
0x007D | 125 | 1 | Input 29 (Slave 7 Input 1) contact status | 0=open, 1=closed
0x007E | 126 | 1 | Input 30 (Slave 7 Input 2) contact status | 0=open, 1=closed
0x007F | 127 | 1 | Input 31 (Slave 7 Input 3) contact status | 0=open, 1=closed
0x0080 | 128 | 1 | Input 32 (Slave 7 Input 4) contact status | 0=open, 1=closed
0x0081 | 129 | 1 | Input 33 (Slave 8 Input 1) contact status | 0=open, 1=closed
0x0082 | 130 | 1 | Input 34 (Slave 8 Input 2) contact status | 0=open, 1=closed
0x0083 | 131 | 1 | Input 35 (Slave 8 Input 3) contact status | 0=open, 1=closed
0x0084 | 132 | 1 | Input 36 (Slave 8 Input 4) contact status | 0=open, 1=closed
0x0085 | 133 | 1 | Input 37 (Slave 9 Input 1) contact status | 0=open, 1=closed
0x0086 | 134 | 1 | Input 38 (Slave 9 Input 2) contact status | 0=open, 1=closed
0x0087 | 135 | 1 | Input 39 (Slave 9 Input 3) contact status | 0=open, 1=closed
0x0088 | 136 | 1 | Input 40 (Slave 9 Input 4) contact status | 0=open, 1=closed
0x0089 | 137 | 1 | Input 41 (Slave 10 Input 1) contact status | 0=open, 1=closed
0x008A | 138 | 1 | Input 42 (Slave 10 Input 2) contact status | 0=open, 1=closed
0x008B | 139 | 1 | Input 43 (Slave 10 Input 3) contact status | 0=open, 1=closed
0x008C | 140 | 1 | Input 44 (Slave 10 Input 4) contact status | 0=open, 1=closed
0x008D | 141 | 1 | Input 45 (Slave 11 Input 1) contact status | 0=open, 1=closed
0x008E | 142 | 1 | Input 46 (Slave 11 Input 2) contact status | 0=open, 1=closed
0x008F | 143 | 1 | Input 47 (Slave 11 Input 3) contact status | 0=open, 1=closed
0x0090 | 144 | 1 | Input 48 (Slave 11 Input 4) contact status | 0=open, 1=closed
0x0091 | 145 | 1 | Input 49 (Slave 12 Input 1) contact status | 0=open, 1=closed
0x0092 | 146 | 1 | Input 50 (Slave 12 Input 2) contact status | 0=open, 1=closed
0x0093 | 147 | 1 | Input 51 (Slave 12 Input 3) contact status | 0=open, 1=closed
0x0094 | 148 | 1 | Input 52 (Slave 12 Input 4) contact status | 0=open, 1=closed
0x0095 | 149 | 1 | Input 53 (Slave 13 Input 1) contact status | 0=open, 1=closed
0x0096 | 150 | 1 | Input 54 (Slave 13 Input 2) contact status | 0=open, 1=closed
0x0097 | 151 | 1 | Input 55 (Slave 13 Input 3) contact status | 0=open, 1=closed
0x0098 | 152 | 1 | Input 56 (Slave 13 Input 4) contact status | 0=open, 1=closed
0x0099 | 153 | 1 | Input 57 (Slave 14 Input 1) contact status | 0=open, 1=closed
0x009A | 154 | 1 | Input 58 (Slave 14 Input 2) contact status | 0=open, 1=closed
0x009B | 155 | 1 | Input 59 (Slave 14 Input 3) contact status | 0=open, 1=closed
0x009C | 156 | 1 | Input 60 (Slave 14 Input 4) contact status | 0=open, 1=closed
0x009D | 157 | 1 | Input 61 (Slave 15 Input 1) contact status | 0=open, 1=closed
0x009E | 158 | 1 | Input 62 (Slave 15 Input 2) contact status | 0=open, 1=closed
0x009F | 159 | 1 | Input 63 (Slave 15 Input 3) contact status | 0=open, 1=closed
0x00A0 | 160 | 1 | Input 64 (Slave 15 Input 4) contact status | 0=open, 1=closed
0x00A1 | 161

## Holding Registers
Holding Registers, 16-bit data, read or write |  |  |  | Functions: Read = 0x03, Write = 0x06, Write Multiple = 0x10
Register |  | Length | Description | Units or Valid Values | B1001 name | Implementation Version
Hexadecimal | Decimal
0x0001 | 1 | 1 | Alarm types 0 to 15 | The least Significant bit of the register represents alarm 0 (Monoblock Chg/Dis Voltage), Most significant bit represents alarm 15.
0x0002 | 2 | 1 | Alarm types 16 to 31 | The least Significant bit of the register represents alarm 16 (Long term memory full), Most significant bit represents alarm 31.
0x0003 | 3 | 1 | Input alarms 1 to 16 | Status of Input alarms for the Master Sentinel and Slave Sentinels 1, 2 and 3.
Bit 0 = Master Input 1 alarm
Bit 1 = Master Input 2 alarm
Bit 2 = Master Input 3 alarm
Bit 3 = Master Input 4 alarm
Bit 4 = Slave 1 Input 1 alarm
Bit 5 = Slave 1 Input 2 alarm
Bit 6 = Slave 1 Input 3 alarm
Bit 7 = Slave 1 Input 4 alarm
Bit 8 = Slave 2 Input 1 alarm
Bit 9 = Slave 2 Input 2 alarm
Bit 10 = Slave 2 Input 3 alarm
Bit 11 = Slave 2 Input 4 alarm
Bit 12 = Slave 3 Input 1 alarm
Bit 13 = Slave 3 Input 2 alarm
Bit 14 = Slave 3 Input 3 alarm
Bit 15 = Slave 3 Input 4 alarm
0x0004 | 4 | 1 | Input alarms 17 to 32 | Status of Input alarms for Slave Sentinels 4, 5, 6 and 7.
Bit 0 = Slave 4 Input 1 alarm
Bit 1 = Slave 4 Input 2 alarm
Bit 2 = Slave 4 Input 3 alarm
Bit 3 = Slave 4 Input 4 alarm
Bit 4 = Slave 5 Input 1 alarm
Bit 5 = Slave 5 Input 2 alarm
Bit 6 = Slave 5 Input 3 alarm
Bit 7 = Slave 5 Input 4 alarm
Bit 8 = Slave 6 Input 1 alarm
Bit 9 = Slave 6 Input 2 alarm
Bit 10 = Slave 6 Input 3 alarm
Bit 11 = Slave 6 Input 4 alarm
Bit 12 = Slave 7 Input 1 alarm
Bit 13 = Slave 7 Input 2 alarm
Bit 14 = Slave 7 Input 3 alarm
Bit 15 = Slave 7 Input 4 alarm
0x0005 | 5 | 1 | Input alarms 33 to 48 | Status of Input alarms for Slave Sentinels 8, 9, 10 and 11.
Bit 0 = Slave 8 Input 1 alarm
Bit 1 = Slave 8 Input 2 alarm
Bit 2 = Slave 8 Input 3 alarm
Bit 3 = Slave 8 Input 4 alarm
Bit 4 = Slave 9 Input 1 alarm
Bit 5 = Slave 9 Input 2 alarm
Bit 6 = Slave 9 Input 3 alarm
Bit 7 = Slave 9 Input 4 alarm
Bit 8 = Slave 10 Input 1 alarm
Bit 9 = Slave 10 Input 2 alarm
Bit 10 = Slave 10 Input 3 alarm
Bit 11 = Slave 10 Input 4 alarm
Bit 12 = Slave 11 Input 1 alarm
Bit 13 = Slave 11 Input 2 alarm
Bit 14 = Slave 11 Input 3 alarm
Bit 15 = Slave 11 Input 4 alarm
0x0006 | 6 | 1 | Input alarms 49 to 64 | Status of Input alarms for Slave Sentinels 12, 13, 14 and 15.
Bit 0 = Slave 12 Input 1 alarm
Bit 1 = Slave 12 Input 2 alarm
Bit 2 = Slave 12 Input 3 alarm
Bit 3 = Slave 12 Input 4 alarm
Bit 4 = Slave 13 Input 1 alarm
Bit 5 = Slave 13 Input 2 alarm
Bit 6 = Slave 13 Input 3 alarm
Bit 7 = Slave 13 Input 4 alarm
Bit 8 = Slave 14 Input 1 alarm
Bit 9 = Slave 14 Input 2 alarm
Bit 10 = Slave 14 Input 3 alarm
Bit 11 = Slave 14 Input 4 alarm
Bit 12 = Slave 15 Input 1 alarm
Bit 13 = Slave 15 Input 2 alarm
Bit 14 = Slave 15 Input 3 alarm
Bit 15 = Slave 15 Input 4 alarm
0x0100 |  |  | SNMP config data | P2_SNMP_CONFIG_START |  | 5.4.12
0x0100 |  | 1 | DHCP enabled | 1 = on. 0 = off
0x0101 |  | 4 | IP Address | Ipv4 address (left to right, 1 octect per word)
0x0105 |  | 4 | Subnet | Ipv4 subnet
0x0109 |  | 4 | Gateway | Ipv4 gateway
0x010D |  | 1 | Serial Attempts
0x010E |  | 2 | Serial Retries
0x0110 |  | 2 | Sleep Duration | milliseconds
0x0112 |  | 2 | Sleep Minimum Duration | milliseconds
0x0114 |  | 2 | Alarm request interval | seconds
0x0116 |  | 2 | String request interval | seconds
0x0118 |  | 2 | Monoblock request interval | seconds
0x011C |  | 4 | Trap Destination | ipv4 address
0x012C |  | 16 | Trap Community | null terminated string (2 characters per word, MSB right)
0x013C |  | 16 | Read-only Community | null terminated string
0x014C |  | 16 | Write Community | null terminated string
0x015C |  | 16 | System location | null terminated string
0x016C |  | 16 | Spare | spare
0x016D |  | 1 | Spare | spare
P2_SNMP_CONFIG_END