Powerlink Time Sync

# Model B07-061

## Installation Guide

### Introduction

The B07-061 Time Sync Unit is a self-contained time sync signal generator, consisting of an active antenna, GPS receiver and timing signal generation in a peaked enclosure with permanently attached cable exiting from the base.

### Operation

The Time Sync Unit is optimised for timing performance. It takes longer than a conventional GPS unit to get a position fix (often up to 30 minutes) but once it is sure of its position (this requires a minimum of 2.5 hours or uninterrupted operation) it can return very accurate timing from a single GPS satellite. It will retain this position information over a loss of power.

### Mounting

The Time Sync is supplied with a stainless steel mounting bracket and u-bolts for pole mounting. The bracket can be mounted on a pole up to 50mm in diameter, or attached directly to a flat surface so long as it has an unobstructed view of the sky.

### Connections

| Wire | Tracer | Function | Characteristics |
| --- | --- | --- | --- |
| White | Orange | Supply + | 8-30V DC, 250mA max draw. |
| Orange | - | Supply - | Common negative to all signal lines. |
| White | Brown | 1PPS + | Rising edge on-time; 0V/+5V swing; output impedance 50Ω. |
| Brown | - | 1PPS - |  |
| White | Blue | IRIG-B + | Unmodulated 0V/+5V swing unloaded; output impedance 50Ω. |
| Blue | - | IRIG-B - |  |
| White | Green | Tx Data | RS-232 transmit data. Factory use only. |
| Green | - | Rx Data | RS-232 receive data. Factory use only. |
| Foil Screen | Shield | Connect to a good earth point. |

### Specifications

| Dimensions | 102mm diameter, 82mm height |
| --- | --- |
| Case type | Molded UV- resistant plastic conical radome. Aluminum die cast base. |
| Mounting | Stainless steel mounting bracket and pole clamps included. |
| Antenna | Motorola Timing2000 Active Antenna 25 dB gain; <1.5dB typical noise figure; 40dB minimum filtering at +/- 50MHz |
| GPS receiver | Motorola M12+ Oncore Timing in T-RAIM mode |
| Satellite reception | 12-channel |
| Time accuracy | ±5μs on both outputs |
| IRIG-B Options | Standard IRIG-B, Abbey Extended, IEEE-1344; UTC offset (factory setting) |
| Operating temp | -20°C to +70°C |
| Cable | 10 or 25 metres of BELDEN 1421A or AWM 2919. High quality four twisted pairs of stranded wire, with a foil screen, drain wire and reinforcing thread |
| Connector | Unterminated bare cable |
| Ordering | B07-061/10 (10m cable); B07-061/25 (25m cable) |

Copyright © 2006-2011 Abbey Systems Ltd

www.abbey.co.nz

support@abbey.co.nz

Level 3, 220 Willis Street

PO Box 27-497

Wellington, New Zealand

Phone +64-4-385-6611

###### Fax +64-4-3856848

Document Number	IG-638-1.2-2012-Jun

Products Covered	B07-061/xx

Revision Number	1.2

Revision date	14 June 2012

# Comments

Revision History

Rev	Date	By	Description

0.0        2005-07-25      TN        Created the new IG/TN template

1.0        2005-08-23      TN        Started Timesync2 IG

1.1        2011-11-10	      COH	  Updated guide with new Visio diagrams and shifted format over to Word.

Shifted size to single A4 per page to help with PDF printing. (Document can now be easily printed in booklet form using only the printer settings)

1.2       2012-06-14      CO  Changed title to Powerlink Time Sync from TIMESYNC 2 & all references to Timesync changed to Time Sync

# Text boxes

Time Sync Installation Guide	1	IG-638-1.2-2012-Jun

IG-638-1.2-2012-Jun	2	Time Sync Installation Guide